📄 OCEMS Alert Generation & Justification Report

---

## 1. General Information

Plant Name: Green Valley Cement Plant

Unit/Section: Kiln – Main Combustion Chamber

Location: Green Valley Industrial Zone, Country X

Report ID: OCEMS‑2026‑02‑01‑001

Date of Report: 2026‑04‑19

Prepared By: Eng. Maya Patel (Environmental Engineer)

Reviewed By: Eng. Luis Hernández (Process Engineer)

---

## 2. Alert Summary

Alert ID: ALERT‑20260201‑001

Date & Time of Alert: 2026‑02‑01 00:20 hrs

Parameter Triggered: NOx (Nitrogen Oxides)

Measured Value: 911.87 mg/Nm³

Permissible Limit: 500 mg/Nm³ (Regulatory Limit – Category II)

Duration of Exceedance: 10 minutes (00:20 – 00:30 hrs)

Severity Level: Red (Critical)

Mode of Detection: Auto‑generated (OCEMS software)

---

## 3. Instrument & System Details

OCEMS Equipment ID: CEMS‑KILN‑01

Make & Model: ABB CEMS‑5000

Last Calibration Date: 2025‑12‑01

Calibration Due Date: 2026‑12‑01

Instrument Status at Time of Alert: Normal (no fault flags)

Data Availability: Continuous (no gaps recorded)

---

## 4. Process/Operational Conditions

Plant Load (%): 85 % (full production)

Production Status: Normal operation (steady‑state)

Fuel Type & Consumption Rate: Pulverised coal, 1 500 t day⁻¹ (≈ 62.5 t hr⁻¹)

Any Process Upset: No

Weather Conditions (relevant): Ambient temperature 15 °C, wind 3 m s⁻¹ from the north, no precipitation

---

## 5. Root Cause Analysis

Type of Alert: ☐ Genuine Emission Exceedance ✔ Instrument Error ☐ Calibration Drift ☐ Power/Communication Failure ☐ Process Upset ☐ Other (Specify)

Detailed Explanation:

The NOx concentration peaked at 911.87 mg/Nm³ coinciding with a kiln temperature of 320.55 °C and an excess oxygen level of 3.17 % (O₂). Elevated O₂ and high flame temperature promote thermal NOx formation. The simultaneous rise in PM (30.66 mg/Nm³) indicates incomplete combustion of coal particles, further supporting a combustion‑related cause. No instrument fault flags were present, and the calibration certificate (dated 2025‑12‑01) is within the validity period. SCADA logs confirm that the air‑fuel ratio set‑point was inadvertently shifted 5 % richer during the 00:15‑00:30 hrs interval, leading to higher flame temperature and NOx formation. Therefore, the alert is classified as a genuine emission exceedance caused by a temporary combustion control deviation.

---

## 6. Data Validation & Supporting Evidence

Trend Analysis Attached: Yes

Cross‑verification with Manual Sampling: Yes (Manual stack sample at 00:25 hrs returned 920 mg/Nm³ NOx)

Comparison with Adjacent Sensors (if any): Cooler stack NOx not applicable (sensor not installed)

SCADA/PLC Logs Reviewed: Yes (air‑fuel ratio deviation documented)

Screenshots/Graphs Attached: Yes (NOx time‑series, O₂, temperature plots)

---

## 7. Corrective Actions Taken

Immediate Action:

Operator manually restored the air‑fuel ratio set‑point to the nominal value (95 % of design) within 5 minutes of alert generation.

Corrective Measures:

Adjusted the kiln secondary air damper to reduce peak flame temperature.

Initiated a short‑term load reduction to 80 % to stabilise combustion.

Instrument Rectification (if applicable): None required (instrument functioning normally).

Process Adjustments: Updated the combustion control algorithm to include a temperature‑based NOx mitigation logic.

Timeline of Actions:

00:25 hrs – Set‑point corrected (Immediate)

00:30 hrs – Secondary air damper adjusted (Immediate)

01:00 hrs – Load reduction implemented (Within 40 minutes)

02:00 hrs – Control algorithm update validated (Within 2 hours)

---

## 8. Preventive Measures

Steps to Avoid Recurrence:

1. Implement real‑time NOx‑linked alarm on the air‑fuel ratio controller.

2. Introduce a predictive temperature‑NOx model for proactive set‑point optimisation.

Maintenance/Calibration Plan Updates:

Add quarterly functional checks of the O₂ sensor and air‑fuel ratio valve.

Training/Operational Changes:

Conduct a refresher training session for kiln operators on combustion optimisation and alarm response (scheduled 2026‑05‑10).

---

## 9. Justification Statement

“The alert generated on 2026‑02‑01 00:20 hrs for NOx was analyzed and determined to be valid due to a genuine emission exceedance caused by a temporary air‑fuel ratio deviation that raised kiln temperature and oxygen excess. Supporting evidence from instrument diagnostics, the latest calibration certificate, manual stack sampling (920 mg/Nm³), and SCADA logs confirms the exceedance. Immediate corrective actions restored compliance, and preventive measures have been instituted to ensure future adherence to the regulatory limit.”

---

## 10. Compliance Status

Regulatory Reporting Required: Yes

Reported to Authority: Yes (Environmental Agency – Report No. EA‑2026‑02‑001, submitted on 2026‑02‑02)

Final Status: Closed (All corrective and preventive actions completed, NOx levels back within limit)

---

## 11. Attachments

Trend Graphs (NOx, O₂, Temperature)

Calibration Certificate (ABB CEMS‑5000, 2025‑12‑01)

Maintenance Log (Air‑fuel valve inspection – 2026‑01‑28)

Photographic Evidence (Kiln flame visual – 00:22 hrs)

SCADA Screenshots (Air‑fuel ratio deviation, NOx alarm)

---

## 12. Approval & Sign‑off

Prepared By (Name & Signature): Eng. Maya Patel _______________________

Reviewed By (Name & Signature): Eng. Luis Hernández _______________________

Approved By (Environment Head/Plant Head): Mr. Carlos Mendes (Plant Manager) _______________________

Date: 2026‑04‑19